# Embedded Galvanic Anodes, Item SPV.0060.XX

# A  Description

This special provision describes furnishing all labor, materials, and equipment necessary to properly install embedded galvanic anodes in concrete.

# B  Materials

Furnish pre-manufactured galvanic anodes designed for cathodic protection when embedded in concrete and tied to steel reinforcing.  The core of the anode shall consist of a minimum of 1.3 ounces of electrolytic high grade zinc in compliance with ASTM B418 cast around a pair of steel tie wires and encased in a highly alkaline cementitious shell with a pH of 14.  The anodes shall have one side that is less than 1½-inches in height.

Submit the product information to the engineer for approval.  Supply a certification of compliance to the engineer before starting work.  Deliver, store, and handle all materials according to the manufacturer’s instructions.

Use one of the qualified galvanic anode products and manufacturers given below. An equivalent system may be used with the written approval of the Engineer.

Product Name		Manufacturer/Supplier			Telephone Number

Galvashield		Vector Corrosion Technologies		(319) 364-5355

Sentinel		Euclid Chemical Company		(800) 321-7628

Emaco CP Intact	BASF Building Systems		(262) 227-4045

# C  Construction

# C.1  Concrete Repair

Repair the concrete and prepare the exposed reinforcing steel in accordance with Section 509 of the Standard Specifications.  Use Portland cement based repair concrete materials with suitable electrical conductivity.

# C.2  Galvanic Anode Installation

Install embedded galvanic anodes in accordance with manufacturer’s recommendations, as shown on the plans, and as listed in this specification.

C.2.2  Install galvanic anodes to existing reinforcement along the perimeter of the repair at spacing as specified on the plans.  In no case shall the distance between anodes exceed 24 inches.

C.2.3  Provide 3/4-inch clearance between anodes and substrate to allow repair material to encase anode.

C.2.4  Secure the galvanic anodes as close as possible to the patch edge using the anode tie wires.  Tighten the tie wires to allow little or no free movement.

If the anode is to be tied onto a single bar, or if less than 1½-inch of concrete cover is expected, place anode beneath the uncoated bar and secure to reinforcing steel.

If 1½-inch concrete cover will exist over the anode, the anode may be placed at the intersection between two bars and secured to each bar.

# C.3  Electrical Continuity

Confirm electrical connection between anode tie wire and uncoated reinforcing steel with a multi-meter.  The maximum DC resistance shall be 1 Ohm.  Confirm electrical continuity of the exposed uncoated reinforcing steel within the repair area.  Steel reinforcement shall be considered continuous when the DC resistance is 1 Ohm or less.  If necessary, establish the electrical continuity with uncoated steel tie wire.

# C.4  Inspection

The engineer will verify proper installation of the galvanic anodes prior to placement of the concrete.

# D  Measurement

The department will measure Embedded Galvanic Anodes as each individual anode acceptably installed.

# E  Payment

The department will pay for the measured quantities at the contract unit price under the following bid item:

ITEM NUMBER	DESCRIPTION					UNIT

SPV.0060.XX		Embedded Galvanic Anodes				EA

Payment is full compensation for furnishing and for properly installing; and for establishing and checking electrical continuity.

Concrete repair work will be paid for separately.