WisDOT/DTSD/Bureau of Technical Service - Real Estate

Northeast Region

Building Demolition Specifications -- Asbestos Inspection Reports

The asbestos inspection work to be performed under this special provision shall consist of identifying, sampling, measuring, quantifying, testing, and estimating the cost of removal of RACM, Category I and Category II non-friable asbestos containing materials, and/or other hazardous materials.

The hazardous material inspection performed under this contract shall consist of cataloging any hazardous materials on the site to include location, quantity, type, and how stored.  Besides asbestos, hazardous materials may include but not be limited to:

- Batteries

- Lead

- Mercury

- Oil, petroleum based products

- PCB’s (polychlorinated biphenyls)

- Regulated refrigerants and halons - CFC’s (chlorofluorocarbons) and HCFC’s (hydrochlorofluorocarbons)

- Tires

1.	Site investigation:  Both the interior and exterior of each property should be inspected for asbestos, solid hazardous wastes and stored hazardous materials.  Locate and quantify all homogeneous areas of surfacing materials, thermal system insulation and miscellaneous suspect materials, including electrical panels and/or switch boxes, in areas to be demolished.  Note any possible asbestos debris that is present due to deterioration or damage in those areas.  Identify other hazardous contaminants present, such as above or below ground storage tanks or unidentified barrels.

2.	Sampling:  Contractor will take a minimum of three (3) randomly distributed samples of each suspect material found and seal the sample in accordance with state and local regulations.  Plaster/drywall joint compound, floor tile and floor tile mastics on wood substrate, concrete slabs, siding and roofing materials must be sampled in all structures.  Quantify all materials and indicate the condition of any roofing materials, siding and floor tile/mastics as fair, good or poor (note multiple layers).  Destructive sampling must be done to access ducts and/or pipes in walls, chases, and in areas above suspended ceilings.  If ducts and pipes inside walls cannot be inspected, they must be assumed as asbestos containing material.  Quantities of materials assumed to be asbestos containing materials must be listed in the report.

3.	Testing:  Contractor will arrange for the samples to be tested/analyzed using the polarized light microscope (PLM) method at a National Voluntary Laboratory Accreditation Program Lab.  PLM testing should be conducted until the first sample of a suspect material tests positive for asbestos (greater than 1%.)  No additional samples for that material should be tested.  For all friable materials that show asbestos content present, but less than 1%, the inspector shall have the sample set point counted.  Direct the laboratory to stop at the first sample point counted above 1% (do not point count the remaining samples in that set.) If an individual sample in a set of friable samples has asbestos detected, but less than 1%, and the remaining samples in that set are negative (none detected), point count only the sample or samples with asbestos detected.  Samples that are determined to contain less than 1% asbestos are not considered asbestos containing materials.  Proof of lab certification may be requested upon award.

4.	Report:  The contractor will prepare and submit to the Department a report indicating:

- The testing results of samples taken for asbestos on each parcel.  The results should include the sample number, location in the building, their type/description, and square or linear footage or quantity.  Quantify all materials and indicate the condition of any roofing materials, siding and floor tile/mastics as fair, good or poor (note multiple layers).  Quantities of materials assumed to be asbestos containing materials must be listed.

b.	Summarize any other suspect materials found and assumed to contain asbestos, location, description, area dimensions/quantities.

c.	Summarize any other visible hazardous materials on the property.

d.	Summarize any areas that were excluded from sampling that were a result of accessibility issues, such as attics, basement, crawl spaces, etc.

e.	A conclusion as to whether a "friable” asbestos problem does exist at each site.

f.	The name, address, phone number and certification number of the inspector as well as the date of the inspection.

g.	Contractor must provide a separate cost estimate for the removal and disposal of any confirmed asbestos or other reportable hazardous materials.  Such removal shall comply with the requirements of the Environmental Protection Agency (EPA) regulations, National Emission Standards for Asbestos, the Occupational Safety & Health Administration (OSHA) regulations on asbestos removal and all-applicable Wisconsin Department of Natural Resources (DNR) and local government regulations.  The most recent edition of any applicable standard, code or regulation shall be in effect.  Where conflict among the requirements of these specifications should occur, the most stringent shall be followed.  NOTE: Asbestos abatement services are not included in this contract.

5.	Delivery:  Completion of work is typically desired within thirty (30) calendar days after assignment.  Some occasions may require shorter completion times and will be negotiated with the vendor as needed.  Failure to meet agreed upon due dates for completion of work may result in penalties of ½ of 1% (.5%) per business day beyond the due date until the service is completed.  Contractor is to notify the WisDOT northeast region contact as soon as possible of any obstacles prohibiting access to the site.  Extensions of due dates require WisDOT approval.

Buildings to be Moved or Sold:

Not all of the buildings being inspected will eventually be demolished.  Some of them will be salvaged and/or moved.  While we acknowledge that destructive (manual exploratory demolition) sampling is required to comply fully with Wisconsin Department of Natural Resources and US EPA NESHAPS regulations, we ask that the inspector try to avoid unwarranted destruction.  In the event excessive damage is required, the DOT contact person should be notified prior to sampling.

Occupied Buildings - “Limited" Asbestos Inspection Reports:

There should be an understanding by the inspection contractor(s) that, due to tight schedules for some demolition and construction contract lets, situations may arise when we have tenant occupied buildings, but a “limited” asbestos inspection, report and abatement estimate is required prior to vacancy of the building(s).  When this is the case, we must have an inspector willing and able to perform as follows:

a.	Conduct a room-by-room inspection and documentation of visible asbestos containing materials (ACM's) and presumed asbestos containing materials (PACM's).

b.	Where and when able, without exposing occupants to any hazard, pull material bulk samples - sampling and documentation of observable visible suspect materials - from each room using discretion as to sampling from inconspicuous areas of the room.

c.	Submit a limited asbestos inspection report to include identification, location, quantities and estimated cost of abatement of visible and presumed asbestos containing materials.

It is understood that, in order to fully comply with US EPA NESHAPS and/or Wisconsin Department of Natural Resources regulations, due to the limitations placed upon the inspectors during these “limited” asbestos inspections, an additional follow-up exploratory/destructive demolition inspection and report must be completed once the structure becomes unoccupied and prior to mechanical demolition.

WisDOT contact: Xxx Xxxxx